## Feuil1
Component | Fonction | Failure mode | Local effect | Global effect | Failure detection | remark
Temperature and humidity sensor | Measuring temprature | No output | No measurment of the temperature | If all temperature sensors are not working, impossibilty to control the temperature of the room | No measure given | The redundancy of the sensors ensure the control even if some sensors are not working correctly
|  | Erroneous indication | Incorrect measure of the temperature | Can lead to wrong a control of the temperature | The values of the sensor are not consitent with the others temperature sensors
| Measuring humidity | No output | No measurment of the humidity | If all humidity sensors are not working, impossibilty to control the humidity of the room | No measure given
|  | Erroneous indication | Incorrect measure of the humidity | Can lead to wrong a control of the humidity | The values of the sensor are not consitent with the others humidity sensors
Airflow sensor | Measuring velocity of the air | Not measuring airflow | No measurement of the airflow | Impossible to control the airflow | No measure given | Redundancy needed to ensure that can use the fans even if one airflow sensor is not working correctly
|  | Erroneous indication | Incorrect measurment of the aiflow | Can lead to an incorrect use of the fans | The values of the sensor are not consitent with the others airflow sensors of the fan
Fire sensor | Detect fires | Erroneous indication : False positive | A fire is detected but there is no fire | May lead to stop the servors whereas there is no problem and activate anti-fire system which can lead to damage the servers | The values of the sensor are not consitent with the others fire sensors | The redundancy of the sensors ensure the control even if one sensor is not working correctly
|  | Erroneous indication : False negative | A fire is not detected | Can lead to the destruction of the plant because no action is taken to stop the fire (this is a danger for the servers but more important to the human working in the center) | The values of the sensor are not consitent with the others fire sensors
Fans | Create an airflow | Fail to start | The fan does not create an airflow | The servers might not be cooled and thus could suffer some damage | No physical action of the fan after commanding it to strat | As we have 3 fans, we can still cool the servers (eventually put them in s safe state) even if 1 or 2 fans are not working correctly
|  | Erroneous output | The fan is not truning at the desired speed, thus the airflow is not the desired one | The cooling of the servers might not be as desired | The airflow is not the one expected
|  | Fail to stop | The airflow does not stop | The control of the temperature, humidity and airflow might not be as desired | The fan does not stop | It is quite easy to stop it (for example by manualy turning off its power supply)
PLC | Control the cooling system | Fail to work correctly | The control provided by the PLC is not or incorrectly done | The cooling system is not working correctly (or not working at all) | The cooling of the system is not performed correctly
Electrical drive | Power a fan | Erroneous input (decreased) | The drive may not transmit enough power | The servor may not be cooled enough | The fans are not working as desired and the airflow is not the one expected | Its is diffucult without any test to determine if the failure comes from the fans or from the electrical drives.
|  | Erroneous input (increased) | The drive may transmit too much power | The servors may be too cooled and/or the airflow may be too important
|  | Erroneous output (decreased) | Not enough power transmited to the fan | The servor may not be cooled enough
|  | Erroneous output (increased) | Too much power transmetted to the fan | The servors may be too cooled and/or the airflow may be too important
Profibus | Transfer the data from the sensors to the PLC | No data delivered | The PLC can't recieve information from the sensors | The PLC is unable to ensure the control of the cooling | The PLC doesn't get values from the sensors
Ethernet | Communication between PLC and SCADA | No data delivered | The communication between the PLC and the SCADA is impossible | Impossible for operator to know in which state is the pant and to control the cooling system | Communication between PLC and SCADA shut down